## Fixture Count Data Sheet
Date
Name
Street Address
Town
Contact Number:
Contact Email:
Fixture Count Sheet - Residential
Type of Fixture | Total Fixtures | WSFU | Total WSFU
Bathtub, whirlpool bath or combo tub/showers |  | 2 | 0
Shower - Stand alone |  | 2 | 0
Lavatory Sink | 0 | 1 | 0
Kitchen Sink | 0 | 2 | 0
Dishwasher | 0 | 2 | 0
Bar Sink | 0 | 1 | 0
Clothes Washer | 0 | 2 | 0
Laundry Sink | 0 | 3 | 0
Service Sink \ Mop Sink | 0 | 3 | 0
Hose Bib | 0 | 2.5 | 0
Hose Bib, each additional | 0 | 1 | 0
Toilet, 1.6 GPF gravity Tank | 0 | 3 | 0 | Click here for a definition for this fixture
Toliet, 1.6 GPF Flushometer Valve | 0 | 6 | 0 | Click here for a definition for this fixture
Toilet, >1.6 GPF Flushometer Valve | 0 | 8 | 0 | Click here for a definition for this fixture
Urinal*, 1.0 GPF | 0 | 4 | 0 | Click here for a definition for this fixture
Urinal*, greater than 1.0 GPF | 0 | 6 | 0 | Click here for a definition for this fixture
* Typically not used in residential applications
Enter estimated GPM for max. irrigation zone | 0 |  |  | Click here for a definition for this fixture
Total Fixture Value | 0
Estimated Max. GPM | 0 |  |  | Office Use
Estimated Meter Size | 0 |  |  | Date Rec'd:
Service Size Required | 0 | Meter sizes | FV_total | Premise #
Est. meter size for irrigation zone load only | 0 |  |  | Reviewed/Approved by:
Service Size Required for max irrigation zone | 0
|  | 5/8" | 0-28.4
|  | 3/4" | 28.5-37.4
|  | 1" | 37.5-89.4
|  | 1.5" | 89.5-286.4
|  | 2" | 286.5-532.4
|  | 3" | 532.5-1300.4
|  | 4" | 1300.5-3600.4
|  | 6" | 3600.5-8200
Note on E21: A 1.6 GPF water closet is a typical tank\bowl toliet made AFTER 1992 that uses gravity and not a pressure vessel.
Note on E22: A 1.6 GPF water closet is a typical tank\bowl toliet made AFTER 1992 that uses a pressure vessel, not gravity
Note on E23: A >1.6 GPF water closet is a typical tank\bowl toliet made BEFORE 1992 or rated as such that uses a pressure vessel, not gravity
Note on E24: A 1.0 GPF urinal are those urinals made AFTER 1992.Urinals are not common in residential houses
Note on E25: A >1.0 GPF urinal are those urinals made BEFORE 1992. Urinals are not common in residential houses
Note on E27: Irrigation zone loads are not added to fixture counts as it is assumed irrigation use is during 12am - 6am non peak use and is during times when fixtures are not being used. This is to determine if max zone demand exceeds the sized meter

## NJAW Meter Table
Meters
Table 1 Characteristics of Displacement-Type Meters
Meter Size (in.) | * Safe Maximum Operating Capacity (gpm) | ** Recommended Maximum Rate for Continuous Operations (gpm)
1/2 | 15 | 7.5
1/2 x 3/4 | 15 | 7.5
5/8 | 20 | 10
5/8 x 3/4 | 20 | 10
3/4 | 30 | 15
1 | 50 | 25
1.5 | 100 | 50
2 | 160 | 80
*Operations at this flow rate should not exceed 10 percent of usage, or 2 hr in a 24-hour period. The safe maximum operating capacities are the maximum rates of flow at which water should be passed through the meter for only short periods of time and at infrequent intervals. Maximum flow could be destructive if continuous.
** For continuous 24-hr service, displacement meters should not be operated at flows greater than approximately one-half of the safe maximum operating capacities.
Table 2 Operating Characteristics for Class II Compound Meters
Meter Size (in.) | Safe Maximum Operating Capacity (gpm) | Maximum Flow Rate for Continuous Duty (gpm)
2 | 160 | 80
3 | 350 | 175
4 | 600 | 300
6 | 1350 | 675
8 | 1600 | 900